Hand Sanitiser with 70% alcohol content is classed as a Category 2 Flammable Liquid and strict storage and control arrangements must be adhered to.

- A DSEAR assessment must be undertaken for the storage of any flammable liquid by the PRFS supported by the Fire Safety Team. This must be shared and briefed to all relevant staff.

- The PRFS must read the following guidance and share with all relevant parties;

- HSE Guidance on Storage of Flammable Liquids in Containers https://www.hse.gov.uk/PuBns/priced/hsg51.pdf

- HSE Guidance on Safe Use and Handling of Flammable Liquids https://www.hse.gov.uk/pubns/priced/hsg140.pdf

- HSE Guidance on Dangerous Substances and Explosive Atmospheres https://www.hse.gov.uk/pubns/priced/l138.pdf

- Containers must be stored external to any occupied building in an unenclosed area. This ideally should be external to the premises however; internal roadways and compounds can be considered. Where this is not possible further guidance is given below.

- Where unenclosed storage is not possible the following must be adhered to;

  - Prior approval from the Fire Safety Engineer is required.

  - Storage must be within 30min fire resisting enclosure.

  - Storage rooms must be dedicated for the storage of flammable liquid and no other material.

  - Storage rooms must be bunded or the use of the cabinets below can be utilised.

  - Storage rooms must not be used for anything other than storage including decanting of flammable liquid.

  - Ventilation calculations must be completed to demonstrate that room has adequate ventilation (either natural or mechanical)

- Unless being stored in a dedicated storage room with the above control measures, containers must be stored in a fire resisting cabinets such as the one below, these cabinets must not be used for the storage of any other dangerous or other substance.

  - Cabinets must be bonded / grounded to prevent ignition sources from static.

  - Cabinets must have adequate bunding / sump to catch any spillages arising from 1 full container.

  - Cabinets must not be overfilled, and storage must not inhibit the ventilation.

- There must be emergency procedures in place for spillages and staff must be trained on these.

- A 9 Litre AR-AFFF fire extinguisher should be in situ near storage area. Must be alcohol resisting foam.

- A maximum of 1000L of flammable liquid is permitted at any one site.

- No combustible material should be stored within 2m of external storage, all packing material must be removed.

- No HV or LV cables within 3m of external storage areas

- Due to vapours being heavier than air, no storage is permitted in basement or underground areas or within 2m of any open drain, gulley or catch pit / inspection covers.

- Consideration must be made where larger containers are to be decanted into smaller containers (ie dispensers). This cannot be completed in the same location as internal storage and must have adequate measures for preventing spillages and collecting drips. Ventilation must be sufficient to prevent a build-up of flammable vapour (min 10 air changes an hour). A Work Activity Risk Assessment and Safe System of Work should be documented and briefed to all relevant staff.

- No storage of flammable liquid is permitted in any volume other than areas identified within the DSEAR.

- Signage must be installed as per below on both the entrance to the storage area and on the storage cabinet.

MATERIAL SAFETY DATA SHEET — 16 Sections

SECTION 1 — CHEMICAL PRODUCT AND COMPANY IDENTIFICATION

| Product Identifier Hand Sanitiser |  |  |  | [WHMIS Classification] Flammable Liquids – Cat 2 |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Product Use External use only – apply small amount to area to be sanitised and rub together. |  |  |  |  |  |  |
| Manufacturer’s Name Summerhall Distillery Ltd |  |  | Supplier’s Name |  |  |  |
| Street Address 1 Summerhall |  |  | Street Address |  |  |  |
| City Edinburgh |  | Province City of Edinburgh | City |  |  | Province |
| Postal Code EH9 1PL | Emergency Telephone 0131 2902901 |  | Postal Code |  | Emergency Telephone |  |
| Date MSDS Prepared 01/04/2020 |  | MSDS Prepared By D Quinnell |  | Phone Number 0131 2902901 |  |  |

SECTION 2 — COMPOSITION/INFORMATION ON INGREDIENTS

| Hazardous Ingredients (specific) | % by weight | CAS Number |
| --- | --- | --- |
| Ethanol | 70 | 64-17-5 |
| Hydrogen Peroxide | 4.17 | 7722-84-1 |
| Glycerol | 1.45 | 56-81-5 |

SECTION 3 — HAZARDS IDENTIFICATION

Keep away from heat/sparks/open flames/hot surfaces. — No smoking Keep container tightly closed Ground/bond container and receiving equipment Use explosion-proof equipment Use only non-sparking tools Take precautionary measures against static discharge Wear protective gloves/protective clothing/eye protection/face protection

SECTION 4 — FIRST AID MEASURES

Skin Contact

If skin irritation occurs, rinse affected area with water

Eye Contact

Rinse immediately with plenty of water, also under the eyelids, for at least 15 minutes.

Inhalation

Remove to fresh air

Ingestion

Dilute by giving a large amount of water. Call a physician or Poison Control Center.

SECTION 5 — FIRE FIGHTING MEASURES

| Flammable ❐Yes | If yes, under which conditions? All |  |
| --- | --- | --- |
| Means of Extinction Carbon dioxide (CO2). Alcohol resistant foam. Dry chemical. |  |  |
| Flashpoint (° C) and Method 21 | Upper Flammable Limit (% by volume) Not established | Lower Flammable Limit (% by volume) Not established |
| Autoignition Temperature (°C) 365 °C | Explosion Data — Sensitivity to Impact Not established | Explosion Data — Sensitivity to Static Discharge Not established |
| Hazardous Combustion Products Ethanol |  |  |

SECTION 6 — ACCIDENTAL RELEASE MEASURES

Personal precautions, protective equipment and emergency procedures

Personal Precautions 		Use personal protective equipment as required.

Environmental Precautions 	See Section 12 for additional Ecological Information.

Methods and material for containment and cleaning up

Methods for Containment 		Prevent further leakage or spillage if safe to do so

SECTION 7 — HANDLING AND STORAGE

Precautions for safe handling

Advice on Safe Handling 	Keep away from heat/sparks/open flames/hot surfaces. — No smoking. Use spark-proof tools and explosion-proof equipment. Ground/bond container and receiving equipment. Take precautionary measures against static discharges.

Conditions for safe storage, including any incompatibilities

Storage Conditions 	Keep containers tightly closed in a dry, cool and well-ventilated place. Do not contaminate food or feed stuffs. Do not reuse container. Keep out of the reach of children.

Incompatible Materials 	Strong oxidizers. Hydrogen peroxide. Bromine. Chromic acid.

SECTION 8 — EXPOSURE CONTROL / PERSONAL PROTECTION

Exposure Guidelines

Chemical Name 		ACGIH TLV 		OSHA PEL 			NIOSH IDLH

Ethanol 64-17-5 		STEL: 1000 ppm 	TWA: 1000 ppm 		IDLH: 3300 ppm

TWA: 1900 mg/m3 		TWA: 1000 ppm

(vacated) TWA: 1000 ppm 	TWA: 1900 mg/m3

(vacated) TWA: 1900 mg/m3

Chemical Name 		ACGIH TLV 		OSHA PEL

Glycerol 56-81-5 		TWA: 10 mg/m3 mist 	TWA: 15 mg/m3 mist, total particulate

TWA: 5 mg/m3 mist, respirable fraction

(vacated) TWA: 10 mg/m3 mist, total particulate

(vacated) TWA: 5 mg/m3 mist, respirable fraction

Appropriate engineering controls

Engineering Controls 	Apply technical measures to comply with the occupational exposure limits. Ventilation systems.

Individual protection measures, such as personal protective equipment

Eye/Face Protection 			Avoid contact with eyes.

Skin and Body Protection 		No special technical protective measures are necessary.

Respiratory Protection 			No protective equipment is needed under normal use conditions.

General Hygiene Considerations 	Do not get in eyes. Keep away from food and drink.

SECTION 9 — PHYSICAL AND CHEMICAL PROPERTIES

Information on basic physical and chemical properties

Physical State 		Gel

Appearance 		Clear colourless liquid

Odor 			Alcohol

Color 			Clear

Odor Threshold 	Not determined

Property 				Values 				Remarks • Method

pH 					6.00-8.00

Melting Point/Freezing Point 		Not established

Boiling Point/Boiling Range 		100 °C / 212 °F

Flash Point 				21 °C / 70 °F 			SETA

Evaporation Rate 			Not established

Flammability (Solid, Gas) 		Not determined

Upper Flammability Limits 		Not determined

Lower Flammability Limit		Not determined

Vapor Pressure 			Not established

Vapor Density 				Not established

Specific Gravity				.858 - .882

Water Solubility 			Completely soluble

Solubility in other solvents 		Not determined

Partition Coefficient 			Not determined

Autoignition Temperature 		Not determined

Decomposition Temperature 		Not determined

Explosive Properties 			Not determined

Oxidizing Properties 			Not determined

SECTION 10 — STABILITY AND REACTIVITY

Reactivity 				Not reactive under normal conditions.

Chemical Stability 			Stable under recommended storage conditions.

Possibility of Hazardous Reactions 	None under normal processing.

Hazardous Polymerization		Hazardous polymerization does not occur.

Conditions to Avoid			Keep out of reach of children.

Incompatible Materials 		Strong oxidizers. Hydrogen peroxide. Bromine. Chromic acid.

Hazardous Decomposition Products 	Carbon oxides.

SECTION 11 — TOXICOLOGICAL INFORMATION

Information on likely routes of exposure

Product Information

Eye Contact 	Avoid contact with eyes.

Skin Contact 	Not expected to be a skin irritant during prescribed use.

Inhalation 	Avoid breathing vapors or mists.

Ingestion 	Do not taste or swallow

SECTION 12 — ECOLOGICAL INFORMATION

Ecotoxicity 				Toxic to aquatic life with long lasting effects.

Persistence/Degradability 		Not determined

Bioaccumulation 			Not determined

Mobility

Chemical Name 		Partition Coefficient

Ethanol 64-17-5			-0.32

Other Adverse Effects 			Not determined

SECTION 13 — DISPOSAL CONSIDERATIONS

Waste Treatment Methods

Disposal of Wastes 		Disposal should be in accordance with applicable regional, national and local laws and regulations. Contaminated Packaging 	Disposal should be in accordance with applicable regional, national and local laws and regulations.

SECTION 14 — TRANSPORT INFORMATION

Note: 100ml and 10,000ml containers, is shipped as Limited Quantity

DOT

UN/ID No 		UN1170

Proper Shipping Name 	Ethanol solution

Hazard Class 		3

Packing Group 		II

IATA

UN/ID No 		UN1170

Proper Shipping Name 	Ethanol solution

Hazard Class 		3

Packing Group 		II

IMDG

UN/ID No 		UN1170

Proper Shipping Name 	Ethanol solution

Hazard Class 		3

Packing Group 		II

SECTION 15 — OTHER INFORMATION

Issue Date 08-APR-2020 		Revision Date: 01-APR-2022

Revision Note First Issue

DISCLAIMER: This information relates onto to the specific material designated and may not be valid for such material used in combination with any other materials or in any process. The information and recommendations contained herein are to the best of the manufacturer’s knowledge and belief accurate and reliable as of the date indicated. No representation warranty or guarantee, however, is made with regards to accuracy, reliability or completeness. Conditions of use of the material are under the control of the user; therefore, it is the user’s responsibility to satisfy itself as to the suitability and completeness of such information for its own particular use. Appropriate warnings and safe-handling procedures should be provided to handlers and users.